# Harrow Creek Water Treatment Plant

# 1 Design Basis

The Harrow Creek Water Treatment Plant is sized for a design flow of 25.9 MGD (average day) and a peak flow of 42.2 MGD on the maximum day, serving a population of 42,680 persons.

Measured over five years, the 95th percentile raw water turbidity is 37.6 NTU. Finished water turbidity shall not exceed 0.23 NTU in 95% of monthly samples.

# 2 Treatment Process

The rapid mix basin provides a detention time of 53 s at design flow, with a velocity gradient of 922 1/s.

There are 2 sedimentation basins, each 159 ft long and 47 ft wide, with a side water depth of 15.1 ft; the surface loading rate is 0.86 gpm/ft² at design flow.

Filtration uses 8 dual-media filters of 404 ft² each.

Table 1. Raw water pumps

| Tag | Capacity (gpm) | TDH (ft) | Motor (hp) |
| --- | --- | --- | --- |
| P-101A | 5,151 | 96.8 | 267 |
| P-101B | 5,590 | 64.9 | 139 |
| P-101C | 8,542 | 69.6 | 232 |

# 3 Chemical Feed

Alum is dosed at 38.8 mg/L on the average day and up to 55.7 mg/L on the maximum day.

# 4 Disinfection Options

Two options were compared for primary disinfection.

Table 2. Disinfection options

|  | Option A: UV | Option B: chlorine contact |
| --- | --- | --- |
| Capital cost ($M) | 6.35 | 2.82 |
| Annual energy use (MWh/yr) | 771 | n/a |
| Contact time at peak flow (min) | n/a | 49 |

Flocculation follows in 4 stages, for a total detention time of 23.5 min at design flow.

With one filter out of service, the filtration rate is 4.1 gpm/ft².

Chlorine is fed at 3.3 mg/L ahead of the clearwell.