## Slide 1: Lakeshore Hall C: Energy by End Use

## Slide 2: 1 Energy by End Use
Over the cooling season, Hall C's cooling uses 1,375 MWh, its fans 350 MWh and its lighting 200 MWh, as Figure 1 shows month by month. Figure 2 compares the two cooling options' peak loads.
Chart: MWh
| May | June | July | August | September | October
Cooling | 125 | 250 | 325 | 325 | 225 | 125
Fans | 50 | 50 | 100 | 75 | 50 | 25
Lighting | 25 | 25 | 50 | 50 | 25 | 25
Figure 1. Hall C monthly energy by end use, May to October

## Slide 3: 2 Peak Loads
The two options' peak loads follow the season, rising to midsummer and falling after it.
Chart: tons
| May | June | July | August | September | October
Option 1, chilled beams | 250 | 500 | 600 | 550 | 450 | 200
Option 2, VAV baseline | 350 | 650 | 800 | 750 | 400 | 300
Figure 2. Monthly peak cooling load of the two options