## Slide 1: Lakeshore Convention Center: Metered Electricity

## Slide 2: 1 Electricity Use
Over the year the North substation delivered 7,275 MWh and the South substation 3,400 MWh. Figure 1 gives each substation's use month by month.
Chart: MWh
| January | February | March | April | May | June | July | August | September | October | November | December
North substation | 475 | 450 | 475 | 550 | 675 | 775 | 775 | 775 | 675 | 600 | 500 | 550
South substation | 225 | 200 | 250 | 275 | 300 | 350 | 350 | 350 | 325 | 275 | 250 | 250
Figure 1. Monthly electricity use by substation

## Slide 3: 2 Peak Demand
The utility contract caps the center's demand at 3,519 kW. Figure 2 gives each substation's peak demand in each month; the two peaks seldom fall in the same hour, so their sum overstates the center's.
Chart: kW
| January | February | March | April | May | June | July | August | September | October | November | December
North substation | 1750 | 1650 | 1750 | 1950 | 2050 | 2200 | 2250 | 2250 | 2150 | 1950 | 1700 | 1850
South substation | 850 | 850 | 850 | 950 | 1050 | 1050 | 1150 | 1150 | 1000 | 1000 | 850 | 900
Figure 2. Monthly peak demand by substation