## Summary
Harrow Creek Water Treatment Plant

## 1 Design Basis
The Harrow Creek Water Treatment Plant is sized for a design flow of 25.9 MGD (average day) and a peak flow of 42.2 MGD on the maximum day, serving a population of 42,680 persons.
Measured over five years, the 99th percentile raw water turbidity is 37.6 NTU. Finished water turbidity shall not exceed 0.23 NTU in 95% of monthly samples.

## 2 Treatment Process
The rapid mix basin provides a detention time of 53 s at design flow, with a velocity gradient of 922 1/s. Flocculation follows in 4 stages, for a total detention time of 23.5 min at design flow.
There are 2 sedimentation basins, each 159 ft long and 47 ft wide, with a side water depth of 15.1 ft; the surface loading rate is 0.86 gpm/ft² at design flow.
Filtration uses 8 dual-media filters of 404 ft² each. With all filters in service, the filtration rate is 4.1 gpm/ft².
Table 1. Raw water pumps
Tag | Capacity (gpm) | TDH (ft) | Motor (hp)
P-101A | 5151 | 96.8 | 267
P-101B | 5590 | 64.9 | 139
P-101C | 8542 | 69.6 | 232

## 3 Chemical Feed
Alum is dosed at 38.8 mg/L on the average day and up to 55.7 mg/L on the maximum day. Chlorine is fed at 3.3 mg/L ahead of the clearwell.

## 4 Disinfection Options
Two options were compared for primary disinfection.
Table 2. Disinfection options
| Option A: UV | Option B: chlorine contact
Capital cost ($M) | 6.35 | 2.82
Annual energy use (MWh/yr) | 771 | n/a
Contact time at peak flow (min) | n/a | 49