# Harrow Creek WTP: Equipment Schedules

# 1 Equipment

The schedules below list the plant's pumps, blowers and valves at their rated points.

Table 1a. Raw water pumps

| Raw water pumps | Point | Hydraulics |  | Motor |  |
| --- | --- | --- | --- | --- | --- |
|  |  | Capacity (gpm) | TDH (ft) | Power (hp) | Speed (rpm) |
| P-101A | Rated | 7,824 | 134.8 | 292 | 1,679 |
|  | Runout | 9,155 | 89.5 |  |  |
| P-101B | Rated | 8,837 | 62.5 | 264 | 1,160 |
|  | Runout | 11,072 | 46.2 |  |  |
| P-101C | Rated | 7,650 | 132.1 | 177 | 1,657 |
|  | Runout | 9,200 | 104.2 |  |  |

Table 1b. Process air blowers

| Process air blowers | Rated point |  | Motor |  |
| --- | --- | --- | --- | --- |
|  | Airflow (scfm) | Pressure (psig) | Power (hp) | Speed (rpm) |
| B-401 | 2,837 | 6.58 | 49 | 3,153 |
| B-402 | 1,632 | 8.95 | 57 | 3,552 |
| B-403 | 2,164 | 8.27 | 70 | 3,183 |

Table 2. Valve schedule

| Valves | Cv | Rating (psi) | Stroke time (s) |  |
| --- | --- | --- | --- | --- |
|  |  |  | Open | Close |
| V-301 | 605 | 141 | 62.2 |  |
| V-302 | 3,963 | 175 | 45.4 | 52.4 |
| V-303 | 902 | 185 | 48.1 | 48.9 |
| V-304 | 2,754 | 239 | 54.4 | 58.5 |
| V-305 | 1,939 | 266 | 11.8 |  |
| V-306 | 4,528 | 295 | 13.3 | 12.9 |
| V-307 | 4,097 | 288 | 60.2 | 73.9 |
| V-308 | 2,756 | 186 | 86.1 | 102.2 |
| V-309 | 327 | 289 | 51.5 |  |
| V-310 | 2,033 | 297 | 24.2 | 19.4 |
| V-311 | 261 | 196 | 38.6 | 34.4 |
| V-312 | 3,115 | 262 | 31.9 | 32.7 |
| V-313 | 3,515 | 199 | 80.6 |  |
| V-314 | 1,963 | 209 | 25.9 | 26.9 |
| V-315 | 2,388 | 259 | 39.9 | 46.3 |
| V-316 | 2,910 | 125 | 80.4 | 71.9 |
| V-317 | 2,057 | 234 | 15.4 |  |
| V-318 | 3,786 | 154 | 62.8 | 61.4 |
| V-319 | 4,274 | 238 | 31.5 | 31.6 |
| V-320 | 2,346 | 255 | 75.3 | 81.4 |